## xie
I/O
N.ro | Item |  | Label | Modbus Addr (Base 0) | Modbus Addr (Base 1) | Modbus Access | Measure unit | Inf | Sup
Analog Inputs
1 | Analog value IN1 |  | IN1 | 0201h | HR:514 | RW | °C - bar/10 - PSI (0.1 resolution) | -3256.5 | 3256.5
2 | Analog value IN2 |  | IN2 | 0202h | HR:515 | RW | °C - um/10 (0.1 resolution) | -3256.5 | 3256.5
3 | Analog value IN3 |  | IN3 | 0203h | HR:516 | RW | °C - bar/10 - PSI (0.1 resolution) | -3256.5 | 3256.5
4 | Analog value IN4 |  | IN4 | 0204h | HR:517 | RW | °C - bar/10 - PSI (0.1 resolution) | -3256.5 | 3256.5
5 | Analog value IN5 |  | IN5 | 0205h | HR:518 | RW | °C - bar/10 - PSI (0.1 resolution) | -3256.5 | 3256.5
6 | Analog value IN6 (EV3) / IN10 (EVD) |  | IN6 | 0206h | HR:519 | RW | °C - bar/10 - PSI (0.1 resolution) | -3256.5 | 3256.5
7 | Analog value IN7 (EV3) / IN9 (EVD) |  | IN7 | 0207h | HR:520 | RW | °C - bar/10 - PSI (0.1 resolution) | -3256.5 | 3256.5
8 | Analog value IN1 EXP |  | IN1E | 0208h | HR:521 | RW | °C - bar/10 - PSI (0.1 resolution) | -3256.5 | 3256.5
9 | Analog value IN2 EXP |  | IN2E | 0209h | HR:522 | RW | °C - bar/10 - PSI (0.1 resolution) | -3256.5 | 3256.5
10 | Analog value IN3 EXP |  | IN3E | 020Ah | HR:523 | RW | °C - bar/10 - PSI (0.1 resolution) | -3256.5 | 3256.5
11 | Analog value IN4 EXP |  | IN4E | 020Bh | HR:524 | RW | °C - bar/10 - PSI (0.1 resolution) | -3256.5 | 3256.5
12 | Analog value IN5 EXP |  | IN5E | 020Ch | HR:525 | RW | °C - bar/10 - PSI (0.1 resolution) | -3256.5 | 3256.5
13 | Analog value IN10 EXP |  | IN6E | 020Dh | HR:526 | RW | °C - bar/10 - PSI (0.1 resolution) | -3256.5 | 3256.5
14 | Analog value IN9 EXP |  | IN7E | 020Eh | HR:527 | RW | °C - bar/10 - PSI (0.1 resolution) | -3256.5 | 3256.5
Digital Inputs
15 | Digital value IN1 |  | DI1 | 0101h.Bit0 | HR:258.Bit0 | RW |  | 0=Off | 1=On
16 | Digital value IN2 |  | DI2 | 0101h.Bit1 | HR:258.Bit1 | RW |  | 0=Off | 1=On
17 | Digital value IN3 |  | DI3 | 0101h.Bit2 | HR:258.Bit2 | RW |  | 0=Off | 1=On
18 | Digital value IN4 |  | DI4 | 0101h.Bit3 | HR:258.Bit3 | RW |  | 0=Off | 1=On
19 | Digital value IN5 |  | DI5 | 0101h.Bit4 | HR:258.Bit4 | RW |  | 0=Off | 1=On
20 | Digital value IN6 (EV3) / IN10 (EVD) |  | DI6 | 0101h.Bit5 | HR:258.Bit5 | RW |  | 0=Off | 1=On
21 | Digital value IN7 (EV3) / IN9 (EVD) |  | DI7 | 0101h.Bit6 | HR:258.Bit6 | RW |  | 0=Off | 1=On
22 | Digital value IN8 |  | DI8 | 0101h.Bit7 | HR:258.Bit7 | RW |  | 0=Off | 1=On
23 | Digital value IN9 (EV3) / IN7 (EVD) |  | DI9 | 0101h.Bit8 | HR:258.Bit8 | RW |  | 0=Off | 1=On
24 | Digital value IN10 (EV3) / IN6 (EVD) |  | DI10 | 0101h.Bit9 | HR:258.Bit9 | RW |  | 0=Off | 1=On
25 | Digital value IN1 EXP |  | DI1E | 0101h.Bit10 | HR:258.Bit10 | RW |  | 0=Off | 1=On
26 | Digital value IN2 EXP |  | DI2E | 0101h.Bit11 | HR:258.Bit11 | RW |  | 0=Off | 1=On
27 | Digital value IN3 EXP |  | DI3E | 0101h.Bit12 | HR:258.Bit12 | RW |  | 0=Off | 1=On
28 | Digital value IN4 EXP |  | DI4E | 0101h.Bit13 | HR:258.Bit13 | RW |  | 0=Off | 1=On
29 | Digital value IN5 EXP |  | DI5E | 0101h.Bit14 | HR:258.Bit14 | RW |  | 0=Off | 1=On
30 | Digital value IN10 EXP |  | DI6E | 0101h.Bit15 | HR:258.Bit15 | RW |  | 0=Off | 1=On
31 | Digital value IN9 EXP |  | DI7E | 0102h.Bit0 | HR:259.Bit0 | RW |  | 0=Off | 1=On
32 | Digital value IN8 EXP |  | DI8E | 0102h.Bit1 | HR:259.Bit1 | RW |  | 0=Off | 1=On
33 | Digital value IN7 EXP |  | DI9E | 0102h.Bit2 | HR:259.Bit2 | RW |  | 0=Off | 1=On
34 | Digital valueIN6 EXP |  | DI10E | 0102h.Bit3 | HR:259.Bit3 | RW |  | 0=Off | 1=On
35 | Pulse frequency IN8 |  |  | 0103h | HR:260 | RW | Hz | 0 | 1
36 | Pulse frequency IN9 (EV3) / IN7 (EVD) |  |  | 0104h | HR:261 | RW | Hz | 0 | 1
37 | Pulse frequency IN8 EXP |  |  | 0105h | HR:262 | RW | Hz | 0 | 1
38 | Pulse frequency IN7 EXP |  |  | 0106h | HR:263 | RW | Hz | 0 | 1
Analog Outputs
39 | Analog value TK1/OC |  | TK1 | 0182h | HR:387 | RW | % | 0 | 100
40 | Analog value TK2/TK |  | TK2 | 0183h | HR:388 | RW | % | 0 | 100
41 | Analog value AO1 |  | AO1 | 0184h | HR:389 | RW | %-Hz | 0 | 255
42 | Analog value AO2 |  | AO2 | 0185h | HR:390 | RW | %-Hz | 0 | 255
43 | Analog value OC EXP |  | TK1E | 0186h | HR:391 | RW | % | 0 | 100
44 | Analog value TK EXP |  | TK2E | 0187h | HR:392 | RW | % | 0 | 100
45 | Analog value AO1 EXP |  | AO1E | 0188h | HR:393 | RW | %-Hz | 0 | 255
46 | Analog value AO2 EXP |  | AO2E | 0189h | HR:394 | RW | %-Hz | 0 | 255
Digital Outputs
47 | Digital value DO1 |  | DO1 | 0181h.Bit0 | HR:386.Bit0 | RW |  | 0=Off | 1=On
48 | Digital value DO2 |  | DO2 | 0181h.Bit1 | HR:386.Bit1 | RW |  | 0=Off | 1=On
49 | Digital value DO3 |  | DO3 | 0181h.Bit2 | HR:386.Bit2 | RW |  | 0=Off | 1=On
50 | Digital value DO4 |  | DO4 | 0181h.Bit3 | HR:386.Bit3 | RW |  | 0=Off | 1=On
51 | Digital value TK1/OC |  | DO5 | 0181h.Bit4 | HR:386.Bit4 | RW |  | 0=Off | 1=On
52 | Digital value TK2/TK |  | DO6 | 0181h.Bit5 | HR:386.Bit5 | RW |  | 0=Off | 1=On
53 | Digital value AN1 |  | DO7 | 0181h.Bit6 | HR:386.Bit6 | RW |  | 0=Off | 1=On
54 | Digital value AN2 |  | DO8 | 0181h.Bit7 | HR:386.Bit7 | RW |  | 0=Off | 1=On
55 | Digital value DO1 EXP |  | DO1E | 0181h.Bit8 | HR:386.Bit8 | RW |  | 0=Off | 1=On
56 | Digital value DO2 EXP |  | DO2E | 0181h.Bit9 | HR:386.Bit9 | RW |  | 0=Off | 1=On
57 | Digital value DO3 EXP |  | DO3E | 0181h.Bit10 | HR:386.Bit10 | RW |  | 0=Off | 1=On
58 | Digital value DO4 EXP |  | DO4E | 0181h.Bit11 | HR:386.Bit11 | RW |  | 0=Off | 1=On
59 | Digital value AN1 EXP |  | DO5E | 0181h.Bit12 | HR:386.Bit12 | RW |  | 0=Off | 1=On
60 | Digital value AN2 EXP |  | DO6E | 0181h.Bit13 | HR:386.Bit13 | RW |  | 0=Off | 1=On
61 | Digital value OC EXP |  | DO7E | 0181h.Bit14 | HR:386.Bit14 | RW |  | 0=Off | 1=On
62 | Digital value TK EXP |  | DO8E | 0181h.Bit15 | HR:386.Bit15 | RW |  | 0=Off | 1=On
STATUS
N.ro | Item |  | Label | Modbus Addr (Base 0) | Modbus Addr (Base 1) | Modbus Access | Measure unit | Inf | Sup
Status
1 | Week day |  |  | 0501h.bits8-15 | HR:1282.bits8-15 | RW |  | 0=Monday | 6=Sunday
[7 empty] | 0 | Monday
[7 empty] | 1 | Tuesday
[7 empty] | 2 | Wednesday
[7 empty] | 3 | Thursday
[7 empty] | 4 | Friday
[7 empty] | 5 | Saturday
[7 empty] | 6 | Sunday
2 | Current Time |  |  | 0500h - 0503h.bits mask[FFFFFFFFh] | HR:1281 - 1284.bits mask[FFFFFFFFh] | RW
3 | Unit Status |  | S01 | 0504h | HR:1285 | RW |  | 0=ON | 2=Stand-by by Digital Input
[7 empty] | 0 | ON
[7 empty] | 1 | Stand-by
[7 empty] | 2 | Stand-by by Digital Input
4 | On Alarm |  | S02 | 0505h | HR:1286 | RW |  | 0=Off | 1=On
5 | Control Probe |  | S03 | 0506h | HR:1287 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0
[7 empty] | -3276.8 | ERR
6 | Actual Setpoint |  | S04 | 0507h | HR:1288 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0
7 | Functioning Mode |  | S05 | 0508h | HR:1289 | RW |  | 0=HP | 4=DHW
[7 empty] | 0 | HP
[7 empty] | 1 | HP + DHW
[7 empty] | 2 | CH
[7 empty] | 3 | CH + DHW
[7 empty] | 4 | DHW
8 | DHW status |  | S06 | 0509h | HR:1290 | RW |  | 0=OFF
[7 empty] | 0 | OFF
[7 empty] | 1 | ON
[7 empty] | 2 | Antilegionella
9 | Antilegionella Holding Time |  | S07 | 050Ah | HR:1291 | RW | s | 0
10 | Antilegionella delay |  | S08 | 050Bh | HR:1292 | RW | d | 0
11 | Thermoregulation Request |  | S09 | 050Ch | HR:1293 | RW | % (0.1 resolution) | 0.0
12 | Actual Steps |  | S10 | 050Dh | HR:1294 | RW |  | 0
13 | Compressor start from pump start delay counter |  | S11 | 050Eh | HR:1295 | RW |  | 0
14 | Pump stop from compressor stop dealay counter |  | S12 | 050Fh | HR:1296 | RW |  | 0
15 | Hot gas bypass regulation status |  | S13 | 0510h | HR:1297 | RW |  | 0=Initialization | 3=Stop
[7 empty] | 0 | Initialization
[7 empty] | 1 | Startup
[7 empty] | 2 | Regulation
[7 empty] | 3 | Stop
16 | Hot gas bypass control valve position |  | S14 | 0511h | HR:1298 | RW | % | 0 | 100
Working Hours
17 | Compressor 1 Working Hours |  | S15 | 0512h | HR:1299 | RW | h*10 | 0
18 | Compressor 2 Working Hours |  | S16 | 0513h | HR:1300 | RW | h*10 | 0
19 | Compressor 3 Working Hours |  | S17 | 0514h | HR:1301 | RW | h*10 | 0
20 | Compressor 4 Working Hours |  | S18 | 0515h | HR:1302 | RW | h*10 | 0
21 | Compressor 5 Working Hours |  | S19 | 0516h | HR:1303 | RW | h*10 | 0
22 | Compressor 6 Working Hours |  | S20 | 0517h | HR:1304 | RW | h*10 | 0
23 | Pump Working Hours |  | S21 | 0518h | HR:1305 | RW | h*10 | 0
24 | Unit Working Hours |  | S22 | 0519h | HR:1306 | RW | h*10 | 0
25 | Fan 1 Working Hours |  | S23 | 051Ah | HR:1307 | RW | h*10 | 0
26 | Fan 2 Working Hours |  | S24 | 051Bh | HR:1308 | RW | h*10 | 0
27 | Fan 3 Working Hours |  | S25 | 051Ch | HR:1309 | RW | h*10 | 0
28 | Fan 4 Working Hours |  | S26 | 051Dh | HR:1310 | RW | h*10 | 0
Circuits status
29 | Circuit 1 Active Steps |  | S27 | 051Eh | HR:1311 | RW |  | 0
30 | Circuit 1 Defrost Status |  | S28 | 051Fh | HR:1312 | RW |  | 0
31 | Circuit 1 Defrost Timer |  | S29 | 0520h | HR:1313 | RW | s | 0
32 | Circuit 1 fan request |  | S30 | 0521h | HR:1314 | RW | % | 0
33 | Circuit 2 Active Steps |  | S31 | 0522h | HR:1315 | RW |  | 0
34 | Circuit 2 Defrost Status |  | S32 | 0523h | HR:1316 | RW |  | 0
35 | Circuit 2 Defrost Timer |  | S33 | 0524h | HR:1317 | RW | s | 0
36 | Circuit 2 fan request |  | S34 | 0525h | HR:1318 | RW | % | 0
Compressors status
37 | Delay Between Defrosts |  | S35 | 0526h | HR:1319 | RW | min | 0
38 | Time between different compressors stops counter |  | S36 | 0527h | HR:1320 | RW | s*10 | 0
39 | Time between different compressors starts counters |  | S37 | 0528h | HR:1321 | RW | s*10 | 0
40 | Activation compressor step delay counter |  | S38 | 0529h | HR:1322 | RW | s*10 | 0
41 | Compressor 1 Circuit |  | S39 | 052Ah | HR:1323 | RW |  | 0=Disabled
[7 empty] | 0 | Disabled
[7 empty] | 1 | Circuit 1
[7 empty] | 2 | Circuit 2
42 | Compressor 1 Active Steps |  | S40 | 052Bh | HR:1324 | RW |  | 0
43 | Compressor 1 Running Countdown |  | S41 | 052Ch | HR:1325 | RW | s*10 | 0
44 | Compressor 2 Circuit |  | S42 | 052Dh | HR:1326 | RW |  | 0=Disabled
[7 empty] | 0 | Disabled
[7 empty] | 1 | Circuit 1
[7 empty] | 2 | Circuit 2
45 | Compressor 2 Active Steps |  | S43 | 052Eh | HR:1327 | RW |  | 0
46 | Compressor 2 Running Countdown |  | S44 | 052Fh | HR:1328 | RW | s*10 | 0
47 | Compressor 3 Circuit |  | S45 | 0530h | HR:1329 | RW |  | 0=Disabled
[7 empty] | 0 | Disabled
[7 empty] | 1 | Circuit 1
[7 empty] | 2 | Circuit 2
48 | Compressor 3 Active Steps |  | S46 | 0531h | HR:1330 | RW |  | 0
49 | Compressor 3 Running Countdown |  | S47 | 0532h | HR:1331 | RW | s*10 | 0
50 | Compressor 4 Circuit |  | S48 | 0533h | HR:1332 | RW |  | 0=Disabled
[7 empty] | 0 | Disabled
[7 empty] | 1 | Circuit 1
[7 empty] | 2 | Circuit 2
51 | Compressor 4 Active Steps |  | S49 | 0534h | HR:1333 | RW |  | 0
52 | Compressor 4 Running Countdown |  | S50 | 0534h | HR:1333 | RW | s*10 | 0
53 | Compressor 5 Circuit |  | S51 | 0536h | HR:1335 | RW |  | 0=Disabled
[7 empty] | 0 | Disabled
[7 empty] | 1 | Circuit 1
[7 empty] | 2 | Circuit 2
54 | Compressor 5 Active Steps |  | S52 | 0537h | HR:1336 | RW |  | 0
55 | Compressor 5 Running Countdown |  | S53 | 0538h | HR:1337 | RW | s*10 | 0
56 | Compressor 6 Circuit |  | S54 | 0539h | HR:1338 | RW |  | 0=Disabled
[7 empty] | 0 | Disabled
[7 empty] | 1 | Circuit 1
[7 empty] | 2 | Circuit 2
57 | Compressor 6 Active Steps |  | S55 | 053Ah | HR:1339 | RW |  | 0
58 | Compressor 6 Running Countdown |  | S56 | 053Bh | HR:1340 | RW | s*10 | 0
Password
59 | Current Level |  | S57 | 053Ch | HR:1341 | RW |  | 0=Hidden
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
60 | Password |  | S58 | 053Dh | HR:1342 | RW |  | -127 | 127
61 | Enable DEMO mode |  | Demo | FF82h | HR:65411 | RW |  | 0=Normal Working | 64=DEMO Mode
[7 empty] | 0 | Normal Working
[7 empty] | 64 | DEMO Mode
PARAMS
N.ro | Item |  | Label | Modbus Addr (Base 0) | Modbus Addr (Base 1) | Modbus Access | Measure unit | Inf | Sup
Setpoint
1 | Cooling mode setpoint |  | Coo | 0600h | HR:1537 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -58.0 | 99.9
2 | Heating mode setpoint |  | HEA | 0601h | HR:1538 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 199.9
3 | DHW setpoint |  | dhU | 0602h | HR:1539 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 199.9
4 | Hot gas bypass setpoint |  | HGb | 0603h | HR:1540 | RW | °C-°F (0.1 resolution) | -58.0 | 99.9
General
5 | Supervision |  | G01 | 0604h | HR:1541 | RW |  | 0 | 255
6 | Regulation start delay from power ON |  | G02 | 0605h | HR:1542 | RW | s | 5 | 255
7 | MODBUS Serial Address |  | G03 | 0606h | HR:1543 | RW |  | 1 | 247
8 | MODBUS Baud Rate |  | G04 | 0607h | HR:1544 | RW |  | 0=2400 | 3=19200
[7 empty] | 0 | 2400
[7 empty] | 1 | 4800
[7 empty] | 2 | 9600
[7 empty] | 3 | 19200
9 | Modbus Parity |  | G05 | 0608h | HR:1545 | RW |  | 0=None | 2=Even
[7 empty] | 0 | None
[7 empty] | 1 | Odd
[7 empty] | 2 | Even
10 | Stop Bits MODBUS |  | G06 | 0609h | HR:1546 | RW |  | 0=1 stop bit | 1=2 stop bits
11 | Measurement Unit |  | G07 | 060Ah | HR:1547 | RW |  | 0=Celsius/Bar | 1=Fahrenheit/Psi
12 | Second line visualization |  | G08 | 060Bh | HR:1548 | RW |  | 0=Time | 15=Setpoint
[7 empty] | 0 | Time
[7 empty] | 1 | AI1
[7 empty] | 2 | AI2
[7 empty] | 3 | AI3
[7 empty] | 4 | AI4
[7 empty] | 5 | AI5
[7 empty] | 6 | AI6(EV3)/AI10(EVD)
[7 empty] | 7 | AI7(EV3)/AI9(EVD)
[7 empty] | 8 | AI1 EXP
[7 empty] | 9 | AI2 EXP
[7 empty] | 10 | AI3 EXP
[7 empty] | 11 | AI4 EXP
[7 empty] | 12 | AI5 EXP
[7 empty] | 13 | AI10 EXP
[7 empty] | 14 | AI9 EXP
[7 empty] | 15 | Setpoint
13 | Sun icon meaning |  | G09 | 060Ch | HR:1549 | RW |  | 0=Heating | 1=Summer
14 | Clock enable |  | G10 | 060Dh | HR:1550 | RW |  | 0=Off | 1=On
15 | Services Password |  | G11 | 060Eh | HR:1551 | RW |  | -127 | 127
16 | Manufacturer Password |  | G12 | 060Fh | HR:1552 | RW |  | -127 | 127
17 | Heating mode enable |  | G13 | 0610h | HR:1553 | RW |  | 0=Off | 1=On
18 | Cooling mode enable |  | G14 | 0611h | HR:1554 | RW |  | 0=Off | 1=On
19 | DHW function enable |  | G15 | 0612h | HR:1555 | RW |  | 0=Off | 1=On
20 | Number of circuits |  | G16 | 0613h | HR:1556 | RW |  | 1 | 2
21 | Number of compressors per circuit |  | G17 | 0614h | HR:1557 | RW |  | 0 | 6
22 | Solenoid valve functioning mode |  | G18 | 0615h | HR:1558 | RW | s | -127 | 127
[7 empty] | 0 | On evaporation probe
23 | Ventilation type |  | G19 | 0616h | HR:1559 | RW |  | 0=Separate | 1=Unique
24 | Enable expansion |  | G20 | 0617h | HR:1560 | RW |  | 0=Off | 1=On
25 | Plant heaters for integration enable |  | G21 | 0618h | HR:1561 | RW |  | 0=Off | 1=On
26 | Hot water use for antifreeze enable |  | G22 | 0619h | HR:1562 | RW |  | 0=Off | 1=On
27 | Dynamic setpoint enable |  | G23 | 061Ah | HR:1563 | RW |  | 0=Off | 1=On
28 | Heat pump switch off for low outdoor temperature |  | G24 | 061Bh | HR:1564 | RW |  | 0=Off | 1=On
29 | Antilegionella mode |  | G25 | 061Ch | HR:1565 | RW |  | 0=Disable | 2=Enable + Power ON
[7 empty] | 0 | Disable
[7 empty] | 1 | Enable
[7 empty] | 2 | Enable + Power ON
Alarm
30 | LP alarm occurrences/hour for manual reset |  | A01 | 061Dh | HR:1566 | RW |  | 0 | 255
31 | LP alarm bypass time |  | A02 | 061Eh | HR:1567 | RW | s | 0 | 255
32 | LP alarm setpoint |  | A03 | 061Fh | HR:1568 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -58.0 | 99.9
33 | LP alarm hysteresis |  | A04 | 0620h | HR:1569 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 99.9
34 | HP alarm occurrences/hour for manual reset |  | A05 | 0621h | HR:1570 | RW |  | 0 | 255
35 | HP alarm setpoint |  | A06 | 0622h | HR:1571 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -58.0 | 99.9
36 | HP alarm hysteresis |  | A07 | 0623h | HR:1572 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 99.9
37 | Number of Flow Switch Alarm Actions per Hour |  | A08 | 0624h | HR:1573 | RW |  | 0 | 255
38 | Flow Switch Alarm Bypass Time |  | A09 | 0625h | HR:1574 | RW | s | 0 | 255
39 | Flow Switch Alarm Delay from Flow Switch Input Activation |  | A10 | 0626h | HR:1575 | RW | s | 0 | 255
40 | Flow Switch Alarm Delay from Flow Switch Input Deactivation |  | A11 | 0627h | HR:1576 | RW | s | 0 | 255
41 | Antifreeze Alarm Bypass Time |  | A12 | 0628h | HR:1577 | RW | s | 0 | 255
42 | Antifreeze Alarm Setpoint |  | A13 | 0629h | HR:1578 | RW | °C-°F | -58 | 99
43 | Antifreeze Alarm Hysteresis |  | A14 | 062Ah | HR:1579 | RW | °C-°F (0.1 resolution) | 0.0 | 99.9
44 | Fan stop for antifreeze alarm |  | A15 | 062Bh | HR:1580 | RW |  | 0=Off | 1=On
45 | High control temperature alarm setpoint |  | A16 | 062Ch | HR:1581 | RW | °C-°F-bar-PSI*10 | -58 | 99
46 | High control temperature alarm delay |  | A17 | 062Dh | HR:1582 | RW | s*10 | 0 | 255
47 | High compressor discharge temperature alarm setpoint |  | A18 | 062Eh | HR:1583 | RW | °C-°F-bar-PSI*10 | 50 | 150
48 | High compressor discharge temperature alarm hysteresis |  | A19 | 062Fh | HR:1584 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 99.9
49 | Fan alarm occurrences/hour for manual reset |  | A20 | 0630h | HR:1585 | RW |  | 0 | 255
50 | Fan alarm bypass time |  | A21 | 0631h | HR:1586 | RW | s | 0 | 255
51 | Maximum Fan Working Hours |  | A22 | 0632h | HR:1587 | RW | h*10 | 0=Disabled | 9999
[7 empty] | 0 | Disabled
52 | Maximum Compressor Working Hours |  | A23 | 0633h | HR:1588 | RW | h*10 | 0=Disabled | 9999
[7 empty] | 0 | Disabled
53 | Pump working hour limit |  | A24 | 0634h | HR:1589 | RW | h*10 | 0=Disabled | 9999
[7 empty] | 0 | Disabled
54 | Compressors termal alarm occurrences/hour for manual reset |  | A25 | 0635h | HR:1590 | RW |  | 0 | 255
55 | Modulating compressor oil recovery setpoint |  | A26 | 0636h | HR:1591 | RW | Hz-% | 0 | 255
56 | Modulating compressor oil recovery delay time |  | A27 | 0637h | HR:1592 | RW | min | 0 | 255
57 | Low outdoor temperature heat pump sutdown setpoint |  | A28 | 0638h | HR:1593 | RW | °C-°F | -58 | 99
58 | Low outdoor temperature heat pump sutdown hysteresis |  | A29 | 0639h | HR:1594 | RW | °C-°F (0.1 resolution) | 0.0 | 99.9
I/O
59 | Control probe configuration |  | I01 | 063Ah | HR:1595 | RW |  | 0=Return probe | 4=Remote control probe 0-10V / 4-20 mA
[7 empty] | 0 | Return probe
[7 empty] | 1 | Supply probe
[7 empty] | 2 | Circuit 1 condensation probe
[7 empty] | 3 | Circuit 1 evaporator probe
[7 empty] | 4 | Remote control probe 0-10V / 4-20 mA
60 | IN1 Input Type Configuration |  | I02 | 063Bh | HR:1596 | RW |  | 0=NTC | 3=0-5 V
[7 empty] | 0 | NTC
[7 empty] | 1 | 4-20 mA
[7 empty] | 2 | 0-10 V
[7 empty] | 3 | 0-5 V
61 | IN2 Input Type Configuration |  | I03 | 063Ch | HR:1597 | RW |  | 0=NTC | 3=0-5 V
[7 empty] | 0 | NTC
[7 empty] | 1 | 4-20 mA
[7 empty] | 2 | 0-10 V
[7 empty] | 3 | 0-5 V
62 | IN1 Expansion Input Type Configuration |  | I04 | 063Dh | HR:1598 | RW |  | 0=NTC | 3=0-5 V
[7 empty] | 0 | NTC
[7 empty] | 1 | 4-20 mA
[7 empty] | 2 | 0-10 V
[7 empty] | 3 | 0-5 V
63 | IN2 Expansion Input Type Configuration |  | I05 | 063Eh | HR:1599 | RW |  | 0=NTC | 3=0-5 V
[7 empty] | 0 | NTC
[7 empty] | 1 | 4-20 mA
[7 empty] | 2 | 0-10 V
[7 empty] | 3 | 0-5 V
64 | IN1 Input Function Configuration |  | I06 | 063Fh | HR:1600 | RW |  | -30=Thermostat step 6 (NC) | 120
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
65 | IN2 Input Function Configuration |  | I07 | 0640h | HR:1601 | RW |  | -30=Thermostat step 6 (NC) | 120
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
66 | IN3 Input Function Configuration |  | I08 | 0641h | HR:1602 | RW |  | -30=Thermostat step 6 (NC) | 120
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
67 | IN4 Input Function Configuration |  | I09 | 0642h | HR:1603 | RW |  | -30=Thermostat step 6 (NC) | 120
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
68 | IN5 Input Function Configuration |  | I10 | 0643h | HR:1604 | RW |  | -30=Thermostat step 6 (NC) | 120
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
69 | IN6 (EV3) / IN10 (EVD) Input Function Configuration |  | I11 | 0644h | HR:1605 | RW |  | -30=Thermostat step 6 (NC) | 120
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
70 | IN7 (EV3) / IN9 (EVD) Input Function Configuration |  | I12 | 0645h | HR:1606 | RW |  | -30=Thermostat step 6 (NC) | 120
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
71 | IN8 Input Function Configuration |  | I13 | 0646h | HR:1607 | RW |  | -30=Thermostat step 6 (NC) | 30
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
72 | IN9 (EV3)/IN7 (EVD) Input Function Configuration |  | I14 | 0647h | HR:1608 | RW |  | -30=Thermostat step 6 (NC) | 30
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
73 | IN10 (EV3)/IN6 (EVD) Input Function Configuration |  | I15 | 0648h | HR:1609 | RW |  | -30=Thermostat step 6 (NC) | 30
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
74 | IN1 Expansion Input Function Configuration |  | I16 | 0649h | HR:1610 | RW |  | -30=Thermostat step 6 (NC) | 120
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
75 | IN2 Expansion Input Function Configuration |  | I17 | 064Ah | HR:1611 | RW |  | -30=Thermostat step 6 (NC) | 120
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
76 | IN3 Expansion Input Function Configuration |  | I18 | 064Bh | HR:1612 | RW |  | -30=Thermostat step 6 (NC) | 120
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
77 | IN4 Expansion Input Function Configuration |  | I19 | 064Ch | HR:1613 | RW |  | -30=Thermostat step 6 (NC) | 120
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
78 | IN5 Expansion Input Function Configuration |  | I20 | 064Dh | HR:1614 | RW |  | -30=Thermostat step 6 (NC) | 120
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
79 | IN10 Expansion Input Function Configuration |  | I21 | 064Eh | HR:1615 | RW |  | -30=Thermostat step 6 (NC) | 120
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
80 | IN9 Expansion Input Function Configuration |  | I22 | 064Fh | HR:1616 | RW |  | -30=Thermostat step 6 (NC) | 120
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
81 | IN8 Expansion Input Function Configuration |  | I23 | 0650h | HR:1617 | RW |  | -30=Thermostat step 6 (NC) | 30
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
82 | IN7 Expansion Input Function Configuration |  | I24 | 0651h | HR:1618 | RW |  | -30=Thermostat step 6 (NC) | 30
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
83 | IN6 Expansion Input Function Configuration |  | I25 | 0652h | HR:1619 | RW |  | -30=Thermostat step 6 (NC) | 30
[7 empty] | -30 | Thermostat step 6 (NC)
[7 empty] | -29 | Thermostat step 5 (NC)
[7 empty] | -28 | Thermostat step 4 (NC)
[7 empty] | -27 | Thermostat step 3 (NC)
[7 empty] | -26 | Thermostat step 2 (NC)
[7 empty] | -25 | Thermostat step 1 (NC)
[7 empty] | -24 | Solar (NC)
[7 empty] | -23 | Generic warning (NC)
[7 empty] | -22 | Generic alarm (NC)
[7 empty] | -21 | Phase sequence relay (NC)
[7 empty] | -20 | Low pressure switch circuit 2 (NC)
[7 empty] | -19 | Low pressure switch circuit 1 (NC)
[7 empty] | -18 | High pressure switch circuit 2 (NC)
[7 empty] | -17 | High pressure switch circuit 1 (NC)
[7 empty] | -16 | Boiler heaters overload (NC)
[7 empty] | -15 | Plant heaters overload (NC)
[7 empty] | -14 | Circuit 2 compressors overload (NC)
[7 empty] | -13 | Circuit 1 compressors overload (NC)
[7 empty] | -12 | Compressor 6 overload (NC)
[7 empty] | -11 | Compressor 5 overload (NC)
84 | Minimum range AI1[@4mA/0V] |  | I26 | 0653h | HR:1620 | RW | bar-PSI*10-V-mA (0.1 resolution) | -15.0 | 300.0
85 | Maximum range AI1[@20mA/10V] |  | I27 | 0654h | HR:1621 | RW | bar-PSI*10-V-mA (0.1 resolution) | -15.0 | 300.0
86 | Minimum range AI2[@4mA/0V] |  | I28 | 0655h | HR:1622 | RW | bar-PSI*10-V-mA (0.1 resolution) | -15.0 | 300.0
87 | Maximum range AI2[@20mA/10V] |  | I29 | 0656h | HR:1623 | RW | bar-PSI*10-V-mA (0.1 resolution) | -15.0 | 300.0
88 | Expansion minimum pressure range IN1[@4mA/0V] |  | I30 | 0657h | HR:1624 | RW | bar-PSI*10-V-mA (0.1 resolution) | -15.0 | 300.0
89 | Expansion maximum pressure range IN1[@20mA/10V] |  | I31 | 0658h | HR:1625 | RW | bar-PSI*10-V-mA (0.1 resolution) | -15.0 | 300.0
90 | Expansion minimum pressure range IN2[@4mA/0V] |  | I32 | 0659h | HR:1626 | RW | bar-PSI*10-V-mA (0.1 resolution) | -15.0 | 300.0
91 | Expansion maximum pressure range IN2[@20mA/10V] |  | I33 | 065Ah | HR:1627 | RW | bar-PSI*10-V-mA (0.1 resolution) | -15.0 | 300.0
92 | IN1 Analogue Input Offset |  | I34 | 065Bh | HR:1628 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -99.9 | 99.9
93 | IN2 Analogue Input Offset |  | I35 | 065Ch | HR:1629 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -99.9 | 99.9
94 | IN3 Analogue Input Offset |  | I36 | 065Dh | HR:1630 | RW | °C-°F (0.1 resolution) | -99.9 | 99.9
95 | IN4 Analogue Input Offset |  | I37 | 065Eh | HR:1631 | RW | °C-°F (0.1 resolution) | -99.9 | 99.9
96 | IN5 Analogue Input Offset |  | I38 | 065Fh | HR:1632 | RW | °C-°F (0.1 resolution) | -99.9 | 99.9
97 | IN6 (EV3)/IN10 (EVD) Analogue Input Offset |  | I39 | 0660h | HR:1633 | RW | °C-°F (0.1 resolution) | -99.9 | 99.9
98 | IN7 (EV3)/IN9 (EVD) Analogue Input Offset |  | I40 | 0661h | HR:1634 | RW | °C-°F (0.1 resolution) | -99.9 | 99.9
99 | IN1 Expansion Analogue Input Offset |  | I41 | 0662h | HR:1635 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -99.9 | 99.9
100 | IN2 Expansion Analogue Input Offset |  | I42 | 0663h | HR:1636 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -99.9 | 99.9
101 | IN3 Expansion Analogue Input Offset |  | I43 | 0664h | HR:1637 | RW | °C-°F (0.1 resolution) | -99.9 | 99.9
102 | IN4 Expansion Analogue Input Offset |  | I44 | 0665h | HR:1638 | RW | °C-°F (0.1 resolution) | -99.9 | 99.9
103 | IN5 Expansion Analogue Input Offset |  | I45 | 0666h | HR:1639 | RW | °C-°F (0.1 resolution) | -99.9 | 99.9
104 | IN10 Expansion Analogue Input Offset |  | I46 | 0667h | HR:1640 | RW | °C-°F (0.1 resolution) | -99.9 | 99.9
105 | IN9 Expansion Analogue Input Offset |  | I47 | 0668h | HR:1641 | RW | °C-°F (0.1 resolution) | -99.9 | 99.9
106 | AO1 Analogue Output Type Configuration |  | I48 | 0669h | HR:1642 | RW |  | 0=Disabled (DO) | 4=Frequency
[7 empty] | 0 | Disabled (DO)
[7 empty] | 1 | Phase cut
[7 empty] | 2 | 0-10V
[7 empty] | 3 | PWM
[7 empty] | 4 | Frequency
107 | AO2 Analogue Output Type Configuration |  | I49 | 066Ah | HR:1643 | RW |  | 0=Disabled (DO) | 4=Frequency
[7 empty] | 0 | Disabled (DO)
[7 empty] | 1 | Phase cut
[7 empty] | 2 | 0-10V
[7 empty] | 3 | PWM
[7 empty] | 4 | Frequency
108 | AO1 Expansion Analogue Output Type Configuration |  | I50 | 066Bh | HR:1644 | RW |  | 0=Disabled (DO) | 4=Frequency
[7 empty] | 0 | Disabled (DO)
[7 empty] | 1 | Phase cut
[7 empty] | 2 | 0-10V
[7 empty] | 3 | PWM
[7 empty] | 4 | Frequency
109 | AO2 Expansion Analogue Output Type Configuration |  | I51 | 066Ch | HR:1645 | RW |  | 0=Disabled (DO) | 4=Frequency
[7 empty] | 0 | Disabled (DO)
[7 empty] | 1 | Phase cut
[7 empty] | 2 | 0-10V
[7 empty] | 3 | PWM
[7 empty] | 4 | Frequency
110 | PWM Output Frequency |  | I52 | 066Dh | HR:1646 | RW | Hz*10 | 1 | 200
111 | Expansion PWM Output Frequency |  | I53 | 066Eh | HR:1647 | RW | Hz*10 | 1 | 200
112 | DO1 Digital Output Function Configuration |  | I54 | 066Fh | HR:1648 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
113 | DO2 Digital Output Function Configuration |  | I55 | 0670h | HR:1649 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
114 | DO3 Digital Output Function Configuration |  | I56 | 0671h | HR:1650 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
115 | DO4 Digital Output Function Configuration |  | I57 | 0672h | HR:1651 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
116 | TK1 (EV3)/OC (EVD) Digital Output Function Configuration |  | I58 | 0673h | HR:1652 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
117 | TK2 Digital Output Function Configuration |  | I59 | 0674h | HR:1653 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
118 | AO1 Digital Output Function Configuration |  | I60 | 0675h | HR:1654 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
119 | AO2 Digital Output Function Configuration |  | I61 | 0676h | HR:1655 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
120 | DO1 Expansion Digital Output Function Configuration |  | I62 | 0677h | HR:1656 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
121 | DO2 Expansion Digital Output Function Configuration |  | I63 | 0678h | HR:1657 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
122 | DO3 Expansion Digital Output Function Configuration |  | I64 | 0679h | HR:1658 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
123 | DO4 Expansion Digital Output Function Configuration |  | I65 | 067Ah | HR:1659 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
124 | AO1 Expansion Digital Output Function Configuration |  | I66 | 067Bh | HR:1660 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
125 | AO2 Expansion Digital Output Function Configuration |  | I67 | 067Ch | HR:1661 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
126 | OC Expansion Digital Output Function Configuration |  | I68 | 067Dh | HR:1662 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
127 | TK2 Expansion Digital Output Function Configuration |  | I69 | 067Eh | HR:1663 | RW |  | -22=Hot gas bypass pulse valve (NC) | 22
[7 empty] | -22 | Hot gas bypass pulse valve (NC)
[7 empty] | -21 | DHW valve (NC)
[7 empty] | -20 | Solar panels pump (NC)
[7 empty] | -19 | DHW tank heater (NC)
[7 empty] | -18 | Plant heaters (NC)
[7 empty] | -17 | Circuit 2 reversing valve (NC)
[7 empty] | -16 | Circuit 1 reversing valve (NC)
[7 empty] | -15 | Circuit 1 fan (step 4)/Circuit 2 fan (step 2)(NC)
[7 empty] | -14 | Circuit 1 fan (step 3)/Circuit 2 fan (step 1)(NC)
[7 empty] | -13 | Circuit 1 fan (step 2)(NC)
[7 empty] | -12 | Circuit 1 fan (step 1)
[7 empty] | -11 | Defrost (NC)
[7 empty] | -10 | Circuit 2 solenoid valve (NC)
[7 empty] | -9 | Circuit 1 solenoid valve (NC)
[7 empty] | -8 | Compressor 6 (NC)
[7 empty] | -7 | Compressor 5 (NC)
[7 empty] | -6 | Compressor 4 (NC)
[7 empty] | -5 | Compressor 3 (NC)
[7 empty] | -4 | Compressor 2 (NC)
[7 empty] | -3 | Compressor 1 (NC)
128 | AO1 Analogue Output Function Configuration |  | I70 | 067Fh | HR:1664 | RW |  | 0=Disabled | 6=Hot gas bypass valve
[7 empty] | 0 | Disabled
[7 empty] | 1 | Pump
[7 empty] | 2 | Circuit 1 compressor
[7 empty] | 3 | Circuit 2 compressor
[7 empty] | 4 | Circuit 1 fans
[7 empty] | 5 | Circuit 2 fans
[7 empty] | 6 | Hot gas bypass valve
129 | AO2 Analogue Output Function Configuration |  | I71 | 0680h | HR:1665 | RW |  | 0=Disabled | 6=Hot gas bypass valve
[7 empty] | 0 | Disabled
[7 empty] | 1 | Pump
[7 empty] | 2 | Circuit 1 compressor
[7 empty] | 3 | Circuit 2 compressor
[7 empty] | 4 | Circuit 1 fans
[7 empty] | 5 | Circuit 2 fans
[7 empty] | 6 | Hot gas bypass valve
130 | AO1 Expansion Analogue Output Function Configuration |  | I72 | 0681h | HR:1666 | RW |  | 0=Disabled | 6=Hot gas bypass valve
[7 empty] | 0 | Disabled
[7 empty] | 1 | Pump
[7 empty] | 2 | Circuit 1 compressor
[7 empty] | 3 | Circuit 2 compressor
[7 empty] | 4 | Circuit 1 fans
[7 empty] | 5 | Circuit 2 fans
[7 empty] | 6 | Hot gas bypass valve
131 | AO2 Expansion Analogue Output Function Configuration |  | I73 | 0682h | HR:1667 | RW |  | 0=Disabled | 6=Hot gas bypass valve
[7 empty] | 0 | Disabled
[7 empty] | 1 | Pump
[7 empty] | 2 | Circuit 1 compressor
[7 empty] | 3 | Circuit 2 compressor
[7 empty] | 4 | Circuit 1 fans
[7 empty] | 5 | Circuit 2 fans
[7 empty] | 6 | Hot gas bypass valve
132 | TK1 Expansion (EV3)/OC (EVD) Analogue Output Function Configuration |  | I74 | 0683h | HR:1668 | RW |  | 0=Disabled | 3=Pump
[7 empty] | 0 | Disabled
[7 empty] | 1 | Circuit 1 fans
[7 empty] | 2 | Circuit 2 fans
[7 empty] | 3 | Pump
[7 empty] | 4 | Hot gas bypass valve
133 | TK2 Analogue Output Function Configuration |  | I75 | 0684h | HR:1669 | RW |  | 0=Disabled | 3=Pump
[7 empty] | 0 | Disabled
[7 empty] | 1 | Circuit 1 fans
[7 empty] | 2 | Circuit 2 fans
[7 empty] | 3 | Pump
[7 empty] | 4 | Hot gas bypass valve
134 | OC Expansion Analogue Output Function Configuration |  | I76 | 0685h | HR:1670 | RW |  | 0=Disabled | 3=Pump
[7 empty] | 0 | Disabled
[7 empty] | 1 | Circuit 1 fans
[7 empty] | 2 | Circuit 2 fans
[7 empty] | 3 | Pump
[7 empty] | 4 | Hot gas bypass valve
135 | TK2 Expansion Analogue Output Function Configuration |  | I77 | 0686h | HR:1671 | RW |  | 0=Disabled | 3=Pump
[7 empty] | 0 | Disabled
[7 empty] | 1 | Circuit 1 fans
[7 empty] | 2 | Circuit 2 fans
[7 empty] | 3 | Pump
[7 empty] | 4 | Hot gas bypass valve
Regulation
136 | Cooling mode control band |  | r01 | 0687h | HR:1672 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 99.9
137 | Heating mode control band |  | r02 | 0688h | HR:1673 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 99.9
138 | DHW control band |  | r03 | 0689h | HR:1674 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 99.9
139 | Control integral time (PI) |  | r04 | 068Ah | HR:1675 | RW | s*10 | 0 | 255
140 | Maximum cooling mode setpoint |  | r05 | 068Bh | HR:1676 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -58.0 | 99.9
141 | Maximum heating mode setpoint |  | r06 | 068Ch | HR:1677 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 199.9
142 | Minimum cooling mode setpoint |  | r07 | 068Dh | HR:1678 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -58.0 | 99.9
143 | Minimim heating mode setpoint |  | r08 | 068Eh | HR:1679 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 199.9
144 | Cooling mode dynamic setpoint offset |  | r09 | 068Fh | HR:1680 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -99.9 | 99.9
145 | Heating mode dynamic setpoint offset |  | r10 | 0690h | HR:1681 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -99.9 | 99.9
146 | Outdoor temperature reference cooling mode dynamic setpoint |  | r11 | 0691h | HR:1682 | RW | °C-°F-bar-PSI*10 | -58 | 99
147 | Outdoor temperature reference heating mode dynamic setpoint |  | r12 | 0692h | HR:1683 | RW | °C-°F-bar-PSI*10 | -58 | 99
148 | Delta outdoor temperature cooling mode dynamic setpoint |  | r13 | 0693h | HR:1684 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -50.0 | 50.0
149 | Delta outdoor temperature heating mode dynamic setpoint |  | r14 | 0694h | HR:1685 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -50.0 | 50.0
150 | Solenoid valve low pressure setpoint |  | r15 | 0695h | HR:1686 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -58.0 | 99.9
151 | Delta setpoint DHW tank heaters for integration |  | r16 | 0696h | HR:1687 | RW | °C-°F (0.1 resolution) | 0.0 | 99.9
152 | DHW function exit bypass time in heating mode |  | r17 | 0697h | HR:1688 | RW | s | 0 | 255
153 | Antilegionella setpoint |  | r18 | 0698h | HR:1689 | RW | °C-°F (0.1 resolution) | 50.0 | 199.9
154 | Antilegionella holding time |  | r19 | 0699h | HR:1690 | RW | min | 0 | 255
155 | Antilegionella interval |  | r20 | 069Ah | HR:1691 | RW | giorni | 1 | 200
156 | Hot gas bypass control dead band |  | r21 | 069Bh | HR:1692 | RW | °C-°F (0.1 resolution) | 0.0 | 99.9
157 | Hot gas bypass control smart band |  | r22 | 069Ch | HR:1693 | RW | °C-°F (0.1 resolution) | 0.0 | 99.9
158 | Hot gas bypass control fast band |  | r23 | 069Dh | HR:1694 | RW | °C-°F (0.1 resolution) | 0.0 | 99.9
159 | Hot gas bypass control proportional band |  | r24 | 069Eh | HR:1695 | RW | °C-°F (0.1 resolution) | 0.1 | 99.9
160 | Hot gas bypass control integral time |  | r25 | 069Fh | HR:1696 | RW | s | 0 | 999
161 | Hot gas bypass control derivative time |  | r26 | 06A0h | HR:1697 | RW | s | 0 | 999
162 | Hot gas bypass control fast action correction factor |  | r27 | 06A1h | HR:1698 | RW | % | 1 | 100
163 | Hot gas bypass control inibition setpoint |  | r28 | 06A2h | HR:1699 | RW | °C-°F | 50 | 150
164 | Hot gas bypass control inibition hysteresis |  | r29 | 06A3h | HR:1700 | RW | °C-°F (0.1 resolution) | 0.0 | 99.9
165 | Hot gas bypass control start delay |  | r30 | 06A4h | HR:1701 | RW | s | 0 | 99
166 | Hot gas bypass control start position |  | r31 | 06A5h | HR:1702 | RW | % | 0 | 100
167 | Hot gas bypass control valve period |  | r32 | 06A6h | HR:1703 | RW | s | 1 | 999
168 | Hot gas bypass control voltage output value |  | r33 | 06A7h | HR:1704 | RW | V (0.1 resolution) | 1.0 | 10.0
Defrost
169 | Refrigeration Circuit Defrost Mode |  | d01 | 06A8h | HR:1705 | RW |  | 0=Off | 3=Time Controlled
[7 empty] | 0 | Off
[7 empty] | 1 | On
[7 empty] | 2 | With Compressor Off
[7 empty] | 3 | Time Controlled
170 | Refrigeration Circuit Defrost Start Setpoint |  | d02 | 06A9h | HR:1706 | RW | °C-°F (0.1 resolution) | -58.0 | 99.9
171 | Delay Refrigeration Circuit Defrost activation |  | d03 | 06AAh | HR:1707 | RW | min | 0 | 255
172 | Refrigeration Circuit Defrost end Setpoint |  | d04 | 06ABh | HR:1708 | RW | °C-°F (0.1 resolution) | -58.0 | 99.9
173 | Maximum Refrigeration Circuit Defrost Time |  | d05 | 06ACh | HR:1709 | RW | min | 0 | 255
174 | Compressor/Reversing Valve Waiting Time from compressor shutdown |  | d06 | 06ADh | HR:1710 | RW | s | 0 | 255
175 | Refrigeration Circuit Drip Time |  | d07 | 06AEh | HR:1711 | RW | s*10 | 0 | 255
176 | Refrigeration Circuit Forced Defrost Start Setpoint |  | d08 | 06AFh | HR:1712 | RW | °C-°F (0.1 resolution) | -58.0 | 99.9
177 | Defrost delay between 2 circuits |  | d09 | 06B0h | HR:1713 | RW | min | 0 | 255
178 | Compressor ON delay during defrost |  | d10 | 06B1h | HR:1714 | RW | s*10 | 0 | 255
179 | Defrost mode fans activation setpoint |  | d11 | 06B2h | HR:1715 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -58.0 | 99.9
180 | Defrost mode fans activation hysteresis |  | d12 | 06B3h | HR:1716 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 99.9
181 | Defrost fan speed |  | d13 | 06B4h | HR:1717 | RW | Hz-% | 0 | 255
Compressors
182 | Number of compressors unloaders |  | C01 | 06B5h | HR:1718 | RW |  | 0 | 5
183 | Compressors Type |  | C02 | 06B6h | HR:1719 | RW |  | 0=ON-OFF | 2=Modulating + ON-OFF
[7 empty] | 0 | ON-OFF
[7 empty] | 1 | Modulating
[7 empty] | 2 | Modulating + ON-OFF
184 | Compressor rotation order/mode |  | C03 | 06B7h | HR:1720 | RW |  | 0=Hour/Saturation | 3=Fixed/Balancing
[7 empty] | 0 | Hour/Saturation
[7 empty] | 1 | Fixed/Saturation
[7 empty] | 2 | Hour/Balancing
[7 empty] | 3 | Fixed/Balancing
185 | Minimum Compressor OFF Time |  | C04 | 06B8h | HR:1721 | RW | s*10 | 0 | 255
186 | Minimum time between same compressor switch-ons |  | C05 | 06B9h | HR:1722 | RW | s*10 | 0 | 255
187 | Minimum time between different compressors switch on |  | C06 | 06BAh | HR:1723 | RW | s*10 | 0 | 255
188 | Minimum time between different compressors stops |  | C07 | 06BBh | HR:1724 | RW | s | 0 | 255
189 | Modulating compressor start-up holding time |  | C08 | 06BCh | HR:1725 | RW | s*10 | 0 | 255
190 | Minimum value modulating compressor |  | C09 | 06BDh | HR:1726 | RW | Hz-% | 10 | 255
191 | Maximum value modulating compressor |  | C10 | 06BEh | HR:1727 | RW | Hz-% | 10 | 255
Fans
192 | Fans start-up time |  | F01 | 06BFh | HR:1728 | RW | s/10 | 0 | 255
193 | Fans phase shift |  | F02 | 06C0h | HR:1729 | RW | ms/2 | 0 | 10
194 | Fans dependence on compressor status |  | F03 | 06C1h | HR:1730 | RW |  | 0=On demand | 1=Independent
195 | Ventilation control delta cut-off |  | F04 | 06C2h | HR:1731 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 99.9
196 | Ventilation control hysteresis cut-off |  | F05 | 06C3h | HR:1732 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 99.9
197 | Cooling mode pre-ventilation time |  | F06 | 06C4h | HR:1733 | RW | s | 0 | 255
198 | Post-ventilation time |  | F07 | 06C5h | HR:1734 | RW | s | 0 | 255
199 | Cooling mode minimum fan speed |  | F08 | 06C6h | HR:1735 | RW | Hz-% | 0 | 100
200 | Heating mode minimum fan speed |  | F09 | 06C7h | HR:1736 | RW | Hz-% | 0 | 100
201 | Cooling mode maximum fan speed |  | F10 | 06C8h | HR:1737 | RW | Hz-% | 0 | 100
202 | Heating mode maximum fan speed |  | F11 | 06C9h | HR:1738 | RW | Hz-% | 0 | 100
203 | Cooling mode maximum silent fan speed |  | F12 | 06CAh | HR:1739 | RW | Hz-% | 0 | 100
204 | Heating mode maximum silent fan speed |  | F13 | 06CBh | HR:1740 | RW | Hz-% | 0 | 100
205 | Cooling mode minimum fan speed setpoint |  | F14 | 06CCh | HR:1741 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -58.0 | 99.9
206 | Heating mode minimum fan speed setpoint |  | F15 | 06CDh | HR:1742 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -58.0 | 99.9
207 | Cooling mode maximum fan speed setpoint |  | F16 | 06CEh | HR:1743 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -58.0 | 99.9
208 | Heating mode maximum fan speed setpoint |  | F17 | 06CFh | HR:1744 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | -58.0 | 99.9
209 | Cooling mode ventilation control band |  | F18 | 06D0h | HR:1745 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 99.9
210 | Heating mode ventilation control band |  | F19 | 06D1h | HR:1746 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 99.9
211 | Fan rotation order |  | F20 | 06D2h | HR:1747 | RW |  | 0=Hour | 1=Fixed
Pump
212 | Pump working mode |  | P01 | 06D3h | HR:1748 | RW |  | 0=Always running | 1=On control demand
213 | Compressor start delay from pump start |  | P02 | 06D4h | HR:1749 | RW | s | 10 | 255
214 | Pump stop delay from compressor stop |  | P03 | 06D5h | HR:1750 | RW | s | 0 | 255
215 | Antifreeze setpoint for pump activation |  | P04 | 06D6h | HR:1751 | RW | °C-°F-bar-PSI*10 | -58 | 99
216 | Antifreeze hysteresis for pump activation |  | P05 | 06D7h | HR:1752 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 99.9
217 | Modulating pump minimum speed |  | P06 | 06D8h | HR:1753 | RW | Hz-% | 0 | 100
218 | Modulating pump setpoint |  | P07 | 06D9h | HR:1754 | RW | °C-°F-bar-PSI*10 | -58 | 99
219 | Modulating pump control band |  | P08 | 06DAh | HR:1755 | RW | °C-°F-bar-PSI*10 (0.1 resolution) | 0.0 | 99.9
Heater
220 | Tank heaters antifreeze setpoint |  | H01 | 06DBh | HR:1756 | RW | °C-°F | -127 | 127
221 | Plant heaters antifreeze setpoint |  | H02 | 06DCh | HR:1757 | RW | °C-°F | -127 | 127
222 | Tank/plant heaters max antifreeze setpoint value |  | H03 | 06DDh | HR:1758 | RW | °C-°F | -127 | 127
223 | Tank/plant heaters min antifreeze setpoint value |  | H04 | 06DEh | HR:1759 | RW | °C-°F | -58 | 127
224 | Tank/plant heaters as integration hysteresis |  | H05 | 06DFh | HR:1760 | RW | °C-°F (0.1 resolution) | 0.0 | 99.9
225 | Activation delay tank/plant heaters for integration |  | H06 | 06E0h | HR:1761 | RW | s*10 | 0 | 255
226 | Delta setpoint plant heaters for integration |  | H07 | 06E1h | HR:1762 | RW | °C-°F (0.1 resolution) | 0.0 | 99.9
Solar Panels
227 | Solar panels setpoint |  | S01 | 06E2h | HR:1763 | RW | °C-°F (0.1 resolution) | 0.0 | 99.9
228 | Solar panels hysteresis |  | S02 | 06E3h | HR:1764 | RW | °C-°F (0.1 resolution) | 0.0 | 99.9
229 | Solar panels high temperature setpoint |  | S03 | 06E4h | HR:1765 | RW | °C-°F | 0 | 255
230 | Solar panels high temperature pump ON time |  | S04 | 06E5h | HR:1766 | RW | s | 0 | 255
231 | Solar panels high temperature pump OFF time |  | S05 | 06E6h | HR:1767 | RW | s | 0 | 255
232 | Solar panels antifreeze setpoint |  | S06 | 06E7h | HR:1768 | RW | °C-°F-bar-PSI*10 | -58 | 99
233 | Solar panels antifreeze hysteresis |  | S07 | 06E8h | HR:1769 | RW | °C-°F (0.1 resolution) | 0.0 | 99.9
234 | Solar DHW setpoint |  | S08 | 06E9h | HR:1770 | RW | °C-°F (0.1 resolution) | -58.0 | 199.9
235 | DHW high temperature setpoint |  | S09 | 06EAh | HR:1771 | RW | °C-°F | 0 | 255
236 | DHW high temperature hysteresis |  | S10 | 06EBh | HR:1772 | RW | °C-°F (0.1 resolution) | 0.0 | 99.9
237 | DHW 3 points valve running time |  | S11 | 06ECh | HR:1773 | RW | s | 0 | 255
Menu visibility
238 | Setpoint menu |  |  | 10EDh | HR:4334 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
239 | Setpoint cool menu |  |  | 10EEh | HR:4335 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
240 | Setpoint heat menu |  |  | 10EFh | HR:4336 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
241 | Setpoint DHW menu |  |  | 10F0h | HR:4337 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
242 | Setpoint HGB menu |  |  | 10F1h | HR:4338 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
243 | menu |  | I/O | 10F2h | HR:4339 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
244 | Analogue inputs menu |  |  | 10F3h | HR:4340 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
245 | Digital inputs menu |  |  | 10F4h | HR:4341 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
246 | Analogue outputs menu |  |  | 10F5h | HR:4342 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
247 | Digital outputs menu |  |  | 10F6h | HR:4343 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
248 | Status menu |  |  | 10F7h | HR:4344 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
249 | Alarms menu |  |  | 10F8h | HR:4345 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
250 | Parameters menu |  |  | 10F9h | HR:4346 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
251 | General parameters menu |  |  | 10FAh | HR:4347 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
252 | Alarm parameters menu |  |  | 10FBh | HR:4348 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
253 | parameters menu |  | I&O | 10FCh | HR:4349 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
254 | Regulation parameters menu |  |  | 10FDh | HR:4350 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
255 | Defrost parameters menu |  |  | 10FEh | HR:4351 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
256 | Compressors parameters menu |  |  | 10FFh | HR:4352 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
257 | parameters menu |  | Fan | 1100h | HR:4353 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
258 | Pump parameters menu |  |  | 1101h | HR:4354 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
259 | Heaters parameters menu |  |  | 1102h | HR:4355 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
260 | Solar panels parameters menu |  |  | 1103h | HR:4356 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
261 | Working hours menu |  |  | 1104h | HR:4357 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
262 | Unit working hours menu |  |  | 1105h | HR:4358 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
263 | Compressor 1 working hours menu |  |  | 1106h | HR:4359 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
264 | Compressor 2 working hours menu |  |  | 1107h | HR:4360 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
265 | Compressor 3 working hours menu |  |  | 1108h | HR:4361 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
266 | Compressor 4 working hours menu |  |  | 1109h | HR:4362 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
267 | Compressor 5 working hours menu |  |  | 110Ah | HR:4363 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
268 | Compressor 6 working hours menu |  |  | 110Bh | HR:4364 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
269 | Pump working hours menu |  |  | 110Ch | HR:4365 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
270 | 1 working hours menu |  | Fan | 110Dh | HR:4366 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
271 | 2 working hours menu |  | Fan | 110Eh | HR:4367 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
272 | 3 working hours menu |  | Fan | 110Fh | HR:4368 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
273 | 4 working hours menu |  | Fan | 1110h | HR:4369 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
274 | Histurian menu |  |  | 1111h | HR:4370 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
275 | Historian visualization menu |  |  | 1112h | HR:4371 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
276 | Delete historian menu |  |  | 1113h | HR:4372 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
277 | Clock menu |  |  | 1114h | HR:4373 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
278 | Year clock menu |  |  | 1115h | HR:4374 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
279 | Month clock menu |  |  | 1116h | HR:4375 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
280 | clock menu |  | Day | 1117h | HR:4376 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
281 | Hour clock menu |  |  | 1118h | HR:4377 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
282 | Minute clock menu |  |  | 1119h | HR:4378 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
283 | Info menu |  |  | 111Ah | HR:4379 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
284 | Password menu |  |  | 111Bh | HR:4380 | RW |  | 0=Hidden | 3=Manufacturer
[7 empty] | 0 | Hidden
[7 empty] | 1 | User
[7 empty] | 2 | Service
[7 empty] | 3 | Manufacturer
INFO
N.ro | Item |  | Label | Modbus Addr (Base 0) | Modbus Addr (Base 1) | Modbus Access | Measure unit | Inf | Sup
Firmware info
1 | Identifier |  |  | FF08h | HR:65289 | R
2 | Variation |  |  | FF09h.bits8-15 | HR:65290.bits8-15 | R
3 | Revision |  |  | FF09h.bits0-7 | HR:65290.bits0-7 | R
4 | Version |  |  | FF04h | HR:65285 | R
ALARMS
N.ro | Item |  | Label | Modbus Addr (Base 0) | Modbus Addr (Base 1) | Modbus Access | Measure unit | Inf | Sup
1 | Remote ON-OFF |  | oFFd | 0301h | HR:770 | R
2 | Flow Alarm |  | AFLo | 0302h | HR:771 | R
3 | High temperature alarm |  | AHtr | 0303h | HR:772 | R
4 | Heat pump disabled |  | AbHP | 0304h | HR:773 | R
5 | Phase sequence alarm |  | APH | 0305h | HR:774 | R
6 | Boiler heater thermal overload alarm |  | ArEb | 0306h | HR:775 | R
7 | Pump overload |  | APMP | 0307h | HR:776 | R
8 | Generic warning |  | Warn | 0308h | HR:777 | R
9 | Generic alarm |  | ALL | 0309h | HR:778 | R
10 | Configuration alarm |  | ACnF | 030Ah | HR:779 | R
11 | Probes error |  | EA | 030Bh | HR:780 | R
12 | Antifreeze alarm |  | AFr | 030Ch | HR:781 | R
13 | Expansion communication alarm |  | ACoM | 030Dh | HR:782 | R
14 | Working hours alarm |  | AHou | 030Eh | HR:783 | R
15 | Alarm 15 |  | AL15 | 030Fh | HR:784 | R
16 | Alarm 16 |  | AL16 | 0310h | HR:785 | R
17 | Circuit 1 high pressure alarm |  | AHP1 | 0311h | HR:786 | R
18 | Circuit 2 high pressure alarm |  | AHP2 | 0312h | HR:787 | R
19 | Circuit 1 low pressure alarm |  | ALP1 | 0313h | HR:788 | R
20 | Circuit 2 low pressure alarm |  | ALP2 | 0314h | HR:789 | R
21 | Circuit 1 fan alarm |  | AF1 | 0315h | HR:790 | R
22 | Circuit 2 fan alarm |  | AF2 | 0316h | HR:791 | R
23 | Circuit 1 compressors thermal overload alarm |  | At1 | 0317h | HR:792 | R
24 | Circuit 2 compressors thermal overload alarm |  | At2 | 0318h | HR:793 | R
25 | Circuit 1 compressors high discharge temperature alarm |  | Ad1 | 0319h | HR:794 | R
26 | Circuit 2 compressors high discharge temperature alarm |  | Ad2 | 031Ah | HR:795 | R
27 | Circuit 1 compressors oil alarm |  | AOi1 | 031Bh | HR:796 | R
28 | Circuit 2 compressors oil alarm |  | AOi2 | 031Ch | HR:797 | R
29 | Alarm 29 |  | AL29 | 031Dh | HR:798 | R
30 | Alarm 30 |  | AL30 | 031Eh | HR:799 | R
31 | Alarm 31 |  | AL31 | 031Fh | HR:800 | R
32 | Alarm 32 |  | AL32 | 0320h | HR:801 | R
33 | Compressor 1 thermal overload alarm |  | AtC1 | 0321h | HR:802 | R
34 | Compressor 2 thermal overload alarm |  | AtC2 | 0322h | HR:803 | R
35 | Compressor 3 thermal overload alarm |  | AtC3 | 0323h | HR:804 | R
36 | Compressor 4 thermal overload alarm |  | AtC4 | 0324h | HR:805 | R
37 | Compressor 5 thermal overload alarm |  | AtC5 | 0325h | HR:806 | R
38 | Compressor 6 thermal overload alarm |  | AtC6 | 0326h | HR:807 | R
39 | Alarm 39 |  | AL39 | 0327h | HR:808 | R
40 | Alarm 40 |  | AL40 | 0328h | HR:809 | R
41 | Compressor 1 high discharge temperature alarm |  | AdS1 | 0329h | HR:810 | R
42 | Compressor 2 high discharge temperature alarm |  | AdS2 | 032Ah | HR:811 | R
43 | Compressor 3 high discharge temperature alarm |  | AdS3 | 032Bh | HR:812 | R
44 | Compressor 4 high discharge temperature alarm |  | AdS4 | 032Ch | HR:813 | R
45 | Compressor 5 high discharge temperature alarm |  | AdS5 | 032Dh | HR:814 | R
46 | Compressor 6 high discharge temperature alarm |  | AdS6 | 032Eh | HR:815 | R
47 | Alarm 47 |  | AL43 | 032Fh | HR:816 | R
48 | Alarm 48 |  | AL44 | 0330h | HR:817 | R
49 | Probe 1 error |  | EA01 | 0331h | HR:818 | R
50 | Probe 2 error |  | EA02 | 0332h | HR:819 | R
51 | Probe 3 error |  | EA03 | 0333h | HR:820 | R
52 | Probe 4 error |  | EA04 | 0334h | HR:821 | R
53 | Probe 5 error |  | EA05 | 0335h | HR:822 | R
54 | Probe 6 error |  | EA06 | 0336h | HR:823 | R
55 | Probe 7 error |  | EA07 | 0337h | HR:824 | R
56 | Expansion probe 1 error |  | EA08 | 0338h | HR:825 | R
57 | Expansion probe 2 error |  | EA09 | 0339h | HR:826 | R
58 | Expansion probe 3 error |  | EA10 | 033Ah | HR:827 | R
59 | Expansion probe 4 error |  | EA11 | 033Bh | HR:828 | R
60 | Expansion probe 5 error |  | EA12 | 033Ch | HR:829 | R
61 | Expansion probe 6 error |  | EA13 | 033Dh | HR:830 | R
62 | Expansion probe 7 error |  | EA14 | 033Eh | HR:831 | R
63 | Alarm 63 |  | AL63 | 033Fh | HR:832 | R
64 | Alarm 64 |  | AL64 | 0340h | HR:833 | R
OTHER ITEMS
N.ro | Item | Label | Modbus Addr (Base 0) | Modbus Addr (Base 1) | Modbus Access | Measure unit | Inf | Sup | Group
No items